Laboratory Animal Medicine 2nd Edition

Chapter 21 Design and Management of Animal Facilities

# Questions

- T or F A primary objective of laboratory animal science is to control variables in the animal’s environment.

- The most difficult parameter to control is:

  - Temperature

  - Cage size

  - Humidity

- An environmental factor that may influence experimental data is:

  - Physical

  - Chemical

  - Microbial

  - All of the above

- T or F A dual-corridor circulation pattern in the animal caging area is better than a single-corridor pattern to reduce chances of cross contamination.

- The most common cubical size is:

  - 4 feet deep by 6 feet wide

  - 7 feet deep by 7 feet wide

  - 7 feet deep by 10 feet wide

- What percentage of the mobile cage racks should the dirty side of the cage sanitizer hold?

  - At least 10 %

  - At least 50 %

  - At least 90 %

- The maximum temperature that feed from natural sources should be stored at is:

  - 70° F (21°C)

  - 50° F (10 °C)

  - 39° F (4° C)

- T or F An ABSL-2 room holding nonhuman primates should maintain negative pressure relative to the corridor.

- What does the acronym HEPA stand for?

- The official definition of a HEPA filter is a filter that removes:

  - 99.97% of particles measuring 0.3 um in diameter

  - 100% of particles measuring 0.4 um in diameter

  - 98% of particles measuring 0.3 um in diameter

- T or F Air supplied to animal rooms should be 100% outside air.

- In a single-corridor conventional facility holding clean and dirty animals, the rooms with the “clean” animals should have a (positive or negative) air balance?

- The standard design temperature range for animal rooms is:

  - 60-70° F

  - 65-85° F

  - 60-90° F

- The generally accepted range for relative humidity control is:

  - 10-50 %

  - 20-40 %

  - 30-70 %

- T or F The “Guide” recommends that rooms housing albino animals be approximately 325 lux (30 foot-candles) at 1.0 m (3.3 ft) above the floor. This level of light appears to be adequate for routine animal care.

- Floor drains in animal rooms should be a minimum of what size?

  - 4” for rodent rooms and 6” for rooms that flush waste

  - 6” for rodent rooms and 8” for rooms that flush waste

  - 6” for rodent rooms and 10” for rooms that flush waste

- T or F  The minimum ceiling height recommended is 10 feet?

- The recommended door size for rooms housing nonhuman primates is:

  - 42 inches wide X 7 ft high

  - 48 inches wide X 8 ft high

  - 60 inches wide X 8 ft high

- T or F Fire alarms that operate between 400 kHz and 500 kHz should be used in facilities housing rodents because most rodent species cannot hear frequencies below 1000 kHz.

- According to the “Guide”, corridors should be:

  - 4-8 ft wide

  - 6-8 ft wide

  - 8-10 ft wide

- Sanitation can be achieved at:

  - 180° F for 1 second

  - 161° F for 15 seconds

  - 143° F for 30 minutes

  - all of the above

- T or F Hyperchlorination has been widely used in the past, but the most common water treatment used for controlling microbial contaminants delivered via water bottles is acidification to a pH of 2.5 -3.0.

- T or F The standard practice is to change cages 1 time per week when using a ventilated microisolation caging system.

- Which type of Biological Safety Cabinet is most commonly used in research animal facilities?

- T or F It is required by the Animal Welfare Act that training must be provided for personnel caring for laboratory animals.

- The LAM book recommends that SOP’s be reviewed how often?

  - Preferably every month, but no less than once every 6 months

  - Preferably every 6 months, but no less that once a year

  - Preferably every year, but no less that every two years

- Name 2 types of cage washers used.

- Name 3 types of animal diets.

- What are the two main types of bedding used?

- In general, how often should animal waste be washed down and primary enclosures sanitized?

Answers:

- T

- c

- d

- T

- a

- a

- a

- T

- High Efficiency Particulate Air

- a

- T

- Positive

- b

- c

- T

- a

- F

- b

- T

- b

- d

- T

- T

- T

- b

- b

- Tunnel, Batch washers

- Closed formula, Open formula, Certified

- Contact, Non-contact

- Wash down runs daily, Sanitize every 2 weeks